## Slide 1: EEE 326
SYNCHRONOUS MACHINE MODULE

## Slide 2: OUTLINE FOR SYNCHRONOUS MACHINES
Types
Construction
Synchronous reactance
Equivalent circuits
Regulation
Steady state operation
Special generators
Synchronous motor
Power factor control and starter
Independent generators
Parallel operation of synchronous generators.

## Slide 3: Key Learning outcomes
Equivalent circuits for motors and generators
Power factor correction using synchronous motors
Parallel operation of synchronous generators

## Slide 4: What are synchronous machines? What types exist?
Electrical machines with a rotor rotating at a speed directly related to the frequency of the current in its stator
Types include:
motors
generators

## Slide 5: What’s the relationship between, speed, frequency and number of poles?
………………………………….(1)
Where
is the rotor speed in rpm
f the source frequency in Hz( in case of a motor) or frequency of the induced voltage (in case of a generator)
P is the number of pole pairs on the rotor

## Slide 6: TYPES of synchronous machines(sm)
Generators
Motors
Most important application of sm is that of a generator(usually 3 phase); also called Alternator
They are the main source of electrical energy
They handle enormous power
They are energy converters
Largest units are those driven by Gas, steam and water power
Motors are used for power factor correction

## Slide 7: CONSTRUCTION – General Information
Essentially the same for motors and generators
They can be used interchangeably albeit that generator are produced to handle larger powers than motors as required by large electrical networks
Also depends on the prime mover(hydropower, steam or gas)
For hydropower operation, a large number of poles are necessary due to slow speed of the rotor; hence the diameters of hydro turbines are large.
For steam or gas operation, the rotor speeds are high and the rotor diameters are small; this limits the magnitude of the forces in the rotor

## Slide 8: CONSTRUCTION – Stator
Similar to that of the squirrel case induction motor
To convert a squirrel case induction motor to a synchronous generator, essentially we change the rotor, ie, replace the rotor of the squirrel case induction motor
The rotor is wound as an electromagnet to carry to carry dc current drawn from an external supply(rather than carrying an ac current)
For small machines a permanent magnet can also be used
Some small machines have stationary field poles and a rotating armature(the part carrying the ac supply current or load current in case of an ac generator)
For large machines(designed to deliver many thousands of volts), the armature is stationary due to difficulties that would arise in insulating the rotor

## Slide 9: CONSTRUCTION – Stator
Stator windings are star connected for insulation reasons
The phase voltage would be of the line voltage
Slot insulation would be reduced
More conductors can be used
Power output shall be larger for a machine of similar dimensions
Justify technically why the stator windings are star connected

## Slide 10: Construction - Rotor
From equation 1, the rotor speed is determined by the number of poles and frequency
The highest operating speed for a synchronous motor is obtained when the number of poles is 2 , implying 1 pole pair
For a frequency of 50/60 Hz, the speed would be 3000/3600 rpm
For variable frequency sources, speeds of 10,000 rpm could be contemplated(example: auxiliary power for aircrafts)
With high speeds; large centripetal forces are produce; these work against the large diameters and protruding pole parts;
Cylindrical Rotors(smooth slotted rotors) are used for steam/gas driven generators which spin at 3000 rpm/3600rpm for 50/60 hz and a pole pair(Small diameter rotors)

## Slide 11: Construction - Cylindrical Rotors(smooth slotted rotors) : characteristics
Small diameter
Long enough to establish the volume required for a given power output
For generators driven by a water turbine, more poles are required due to the reduced speed
This results in a larger rotor diameter(say 10m)
The rotor poles protrude, the windings are concentrated and the airgaps are non uniform

## Slide 12: EXCITATION
Generation of electricity is based on Faraday’s law:
an emf is induced when a time varying field links a conductor
For induction to occur, the magnetic lines of force on the rotor must cut the stator conductors
The lines of force could come from a permanent magnet but for large generators, the rotor field is formed by external injection of current into the pole windings.
Since the rotor is moving with the stator, slip rings and brushes are required
In brushless excitation, (the main field is provided through rotating rectifiers, supplied through induction from another smaller exciter or permanent magnet) neither slip rings nor brushes are use; this allows for less maintenance
WHY DO BRUSHLESS ALTERNATORS UNDERGO LESS MAINTENANCE?

## Slide 13: THEORY OF OPERATION
FIG. 1 : ELEMENTARY SYNCHRONOUS GENERATOR

## Slide 14: THEORY OF OPERATION
Fig 1 is an elementary synchronous generator with 2 poles rotor(permanent magnet or electromagnet) and 3 coils stator
On excitation of the rotor, a sinusoidal space wave is produced on the stator surface
When the rotor turns, it produces a sinusoidal flux linkage with the stator given by equation 2.
From Faraday’s law, equation 2 is modified as in 3

## Slide 15: THEORY OF OPERATION
The peak value of the emf produced is given in equation 4
For a purely sinusoidal waveform, the rms value of the induced voltage can be reduced to the expression in equation 5(For an ideal generator having full pitched coils: 180 electrical degrees apart, and with all the turns concentrated in the same slot); this equation is similar to that of the transformer.
; where = 2ℿf
In practice, and for the purpose of waveform improvement, the windings are distributed and the emfs produced are not in phase.
The induced emf is less than in the ideal case of equation 5

## Slide 16: THEORY OF OPERATION –EMF EQUATIONS
Equation 5 is modified by introducing the coil span factor(also winding pitch, winding factor), as shown in equation 6
For a particular machine, are fixed and fixed
For any change in (increase or decrease) in voltage, we need to change
can be changed by changing the amount of current injected into the rotor circuit()
is changed by changing the field exciter voltage,

## Slide 17: RELATIONSHIP BETWEEN THE STATOR INDUCED EMF AND THE ROTOR FIELD CUNRENT – the open circuit characteristics
GENERATOR OCC

## Slide 18: GENERATOR OCC
It is a relationship between the stator voltage and the rotor field current
This is plotted with the running with no load(open circuit) and at rated(synchronous) speed and varied from zero.
When = 0, some emf can be measured
This is because of residual magnetism(the rotor core retains a little magnetism from the last time field current was passed through the field windings

## Slide 19: PITCH FACTOR AND QUALITY OF THE GENERATED EMF
Pitch Factor or Coil Span Factor is defined as the ratio of emf generated in short pitch coil to the emf generated in full pitch coil OR
the ratio of the voltage induced in a short-pitch winding to the voltage that would be induced if the winding were full pitch.
In general the pitch factor can be determined as in equation 7
……………………………………..(7)
Where n is the order of the harmonic and is the short pitching angle

## Slide 20: Short pitching
Short pitching improves winding waveform
If one slot is shorted in a pole pitch of six(83.3%), the 5th harmonic is removed completely; the 7th harmonic is reduced to 59%.
For star connected stator, the triplen harmonics do not appear at all
Figure 3 shows a diagrammatic representation of short pitching

## Slide 21: Short pitching in Diagram

## Slide 22: How do we further improve the voltage waveform
Coils in the stator are connected together to form a phase band(see fig 4(a) with two adjacent coils distanced by one slot pitch
Because of this phase shift, the phasor sum and the arithmetic sum of the induced voltage are not the same, the latter being higher than the former(see Fig 4(b)

## Slide 23
The phse shift also results in a reduction in the emf
This is accounted for by introducing the Spread, breadth corefficient or distribution factor,
SLOT 1
E
SLOT 3
SLOT 2
E
E
(b)

## Slide 24: Breadth factor defined
The ration of the phasor sum of the emfs to the arithmetic sum
If the induced emf is E
where =
In general,
where is the angular displacement in electrical degrees of the emfs in successive coils in series and n, the number of wound slots per pole per phase

## Slide 25
For a three – phase wound armature with nine slots(3 slots/pole/phase),
n = 3
= 20 electrical degrees
The phase spread
Recall, ,
a constant is introduce to make (5) more realistic for the machine

## Slide 26: SYNCHRONOUS MACHINE EQUIVALENT CIRCUIT – Modelled Equivalent Circuit
A single phase representation shall be used for the purpose of developing the model(albeit that the largest synchronous machines are 3 phase types
For a generator model, the current flowing in the rotor field produces a flux in the air gap and the surface of the stator.
Part of is lost as leakage flux
This leakage adversely affects the saturation conditions of the rotor.
When the stator is loaded, the current flowing in the winding produces a flux,
Part of is lost to leakage flux
This leakage is mainly in the stator slots and the stator winding ends(overhang conductors)
The leakage flux develops a self – induced emf(Reactance emf or Potier reactance)

## Slide 27: Generator Model – Equivalent circuit
This reactance emf appears as a voltage drop, where the leakage reactance.
The generator would have to make up for this voltage drop
The remainder of the armature flux, interacts with the main field flux
The effect is called armature reaction and the associated reactance, is known as armature reactance or magnetising reactance
and usually combine to form the resultant reactance(Synchronous reactance),
Where ……………………………………………….(11)
Note: 1. leakage reactance causes voltage drop
2. the effect of armature reaction on the output of the generator depends on the nature of the load(the power factor)

## Slide 28: Generator Model – Equivalent circuit
The stator of the synchronous machine (like that of the squirrel cage induction motor), has a resistance
A combination of all the impedances is known as Synchronous impedance,
………………………………………………(12)
Fig. 5 shows the modelled equivalent circuit from equation (13)
………………………………....(13)
On no load, ………………………………………….(14)
Where is the internal emf (or the air – gap voltage) that result when the machine is loaded

## Slide 29: Modelled Equivalent Circuit -
Ef
Fig. 5: Synchronous machine Model

## Slide 30: SIMPLIFIED MODEL – class work
Ignore armature resistance
Write the modified version of equation 13
What does the reactance represent
Sketch the modified model
Sketch the phasor diagram of the actual and modified model

## Slide 31: WORKED EXAMPLE 1
A three – phase, star connected alternator supplies a balanced 15 MW, 0.8 power factor(lagging) load. The per phase parameters of the machine are = . If the line voltage at the load is 13.2kV, taking the voltage of one of the phases as reference, calculate the phase and line values of the field e.m.f().
SOLUTION
Given Data
= 132kV, (DO THIS) ;
=
By Kirchoff’s Law
= 8,125.6/ (DO THIS); = = = 7,621V
The line value of = x the phase value (DO THIS)

## Slide 32: SOLUTION TO EXAMPLE 1
f
EQUIVALENT CIRCUIT
PHASOR DIAGRAM

## Slide 33: WORKED EXAMPLE 2
A 600V, 75kVA, Y – connected alternator has = and = . Determine at rated load and unity power factor
(i) the magnetizing reactance(reactance of armature reaction)
(ii) the internal emf,
(iii)the no – load emf,
(DO THIS)
(iii) Recall = (DO THIS); No load line voltage = (DO THIS)

## Slide 34
solution to example 2
Given data: = , = , = 600V, P = 75kVA, = 1.0
(i)
(ii) From equation 13, ; also, = , and (DO THIS)
phase value of (DO THIS); Line value =

## Slide 35: ILLUSTRATION OF THE EFFECT OF POWER FACTOR ON ARMATURE REACTION
Unity pf | Zero pf lagging(pure inductive load) | Zero pf leading(pure capacitive load) | General pf lagging(80% of industrial loads are of the R – L) type | General pf leading(R – C)
Distorts the main flux | Demagnetising effect; output voltage reduced | Magnetising effect, Output voltage increased | Distorts & Demagnetises; effect of reduced output voltage | Distorts & Magnetises; effect of increased output voltage

## Slide 36: SYNCHRONOUS MACHINES CONNECTED TO THE GRID(INFINITE BUS BAR)
Some(small/medium type) synchronous generators as earlier considered are suitable for ISOLATED mode of use
Examples include remote farming communities; stand – by plant for special/sensitive facilities where power security is essential(e.g. computer/Data centers, hospitals[ICUs, theaters, radiographic units, MIRs etc]); manufacturing industries, process plants etc
Largest type SMs are connected as part of a large network of generators – Electricity Grid
This Grid is considered to have:
(i) Constant Voltage
(ii) Zero phase angle
This is shown in Fig. 6(Machine connected to grid)

## Slide 37: SYNCHRONOUS MACHINES CONNECTED TO THE GRID(INFINITE BUS BAR)
Fig. 6: Machine Connected to grid

## Slide 38: DETERMINATION OF THE POWER DELIVERED TO THE BUS BAR
……………………………………………………….(15)
where is the complex conjugate of the armature current
…………………………………………….(16)
…………………………………………(18)

## Slide 39: DETERMINATION OF THE POWER DELIVERED TO THE BUS BAR – CONT’D
The current into the network, is given as in equation 19(i to iv)
………………………………………19(i)
…………………………………...19(ii)
- ……………………..19(iii)
- ……………………..19(iv)

## Slide 40: DETERMINATION OF THE POWER DELIVERED TO THE BUS BAR – CONT’D
Combine equations 15 and 19(iv) to get equation 20
……………………………………………………….(15)
- ……………………..19(iv)
= …………(20)
Equation 20 can be separated into real and imaginary parts to satisfy
S ………………….(21) [SEE EQUATION 22 ON THE NEXT SLIDE TO CONFIRM YOUR ATTEMPT!!!??]

## Slide 41: DETERMINATION OF THE POWER DELIVERED TO THE BUS BAR – CONT’D
From = …………(20)
The Real component,
And
The imaginary component, …..21(ii)
Note
by convention, lagging reactive power(Q) is Positive; Leading reactive power is Negative
if is neglected,

## Slide 42: DETERMINATION OF THE POWER DELIVERED TO THE BUS BAR – CONT’D
Sin ………………………………………………22(i)
Sin ………………………………………………22(ii)
Recall, ……………..(24)
Equation 22(ii) can be rewritten as
Sin ………………………………………………25
Note that both P an T vary sinusoidally with

## Slide 43: DETERMINATION OF THE POWER DELIVERED TO THE BUS BAR – CONT’D
Maximum power, and
Recall

## Slide 44: TUTORIAL EXAMPLE 1/SOLUTION
A Y- connected, two pole, 50Hz, 11kV, 10MVA synchronous generator with = is operating at full load and 0.8 power factor lagging. Calculate
(i) the induced e.m.f and load angle,
(ii) the maximum power, based on the above level of excitation, and
(iii) the maximum torque,

## Slide 45
Given parameters
= ; = 50Hz; = 2
Type of connection = Y
In general the induced emf is given as
in complex form
;

## Slide 46: SOLUTION TO TUTORIAL 1 – cont’d
= = 0.399

## Slide 47
=
But from
Therefore, = - =

## Slide 48: SOLUTION TO TUTORIAL 1 – cont’d
Maximum power,

## Slide 49
((iii)
= 51, 507.4Nm

## Slide 50: SIMPLIFIED MODEL OF A SYNCHRONOUS GENERATOR – How does this simplification affect the phasor diagram?
In this case, the armature resistance is ignored i.e
Fig. 7 : Simplified model of synchronous generator

## Slide 51: TUTORIAL EXAMPLE 2/SOLUTION
Draw the phasor diagrams of a synchronous generator under the following conditions:
(i) lagging power factor
(ii) leading power factor
(iii) maximum power
LAGGING POWER FACTOR PHASOR
j
Fig. 8(i)

## Slide 52: TUTORIAL EXAMPLE 2/SOLUTION – CONT’D
LEADING POWER FACTOR
j
Fig. 8(ii)

## Slide 53: MAXIMUM POWER and
Fig. 8(iii)

## Slide 54: THE SYNCHRONOUS MOTOR
It is not self starting
The rotor oscillates; the rotor pole is attracted, then repulsed as the rotating field sweep past it
This vibration(pole slipping) is unacceptable for its severity
There are two possible ways to solve this problem:

## Slide 55: There are two possible ways to solve this problem:
(i) the rotor is equipped with a squirrel cage winding(damper winding). This enables the rotor to accelerate towards synchronous speed and when close enough, the rotor will ‘lock on’ to the field
(ii) the rotor is driven externally to synchronous speed and when the rotor has locked on, the driving unit is disengaged

## Slide 56: SYNCHRONOUS MOTOR MODEL(EQUIVALENT CIRCUIT) - SIMPLIFIED
Same as that for the generator
The only difference is the direction of the armature current which flows into the machine as shown in Fig . 9

## Slide 57: MOTOR POWER AND OTHER EQUATIONS
VOLTAGE EQUATION
POWER INTO THE MOTOR
Sin (See equation 22(ii))
Derive other relevant equations and draw phasor diagrams as appropriate

## Slide 58: TUTORIAL EXAMPLE 4 - QUESTION
Draw a phasor diagram off a synchronous motor at unity power factor and write down the expressions for and A synchronous machine has the following parameters : , , = 1,
Calculate the excitation voltage, and the load angle , for these conditions.

## Slide 59: SOLUTION
Given Data: , , = 1,
The motor equation is given as
The phasor diagram is as shown:

## Slide 60: SOLUTION TO TUTORIAL 4 CONT’D - TASK 1 : EXCITATION VOLTAGE
Recall
-------------(T4.1)
A

## Slide 61: TASK 1 : EXCITATION VOLTAGE – cont’d
Using T4.1, and = = 231

## Slide 62: TASK 2 – LOAD ANGLE
Recall that
OR
Plug in the values and confirm that
from either of the equations

## Slide 63: TUTORIAL EXAMPLE 5
A synchronous machine has a reactance of . It is excited such that the excitation voltage is twice the the terminal voltage, . Show that its maximum power is given by
What is the power factor at this point point. Draw the phasor diagram.

## Slide 64: SOLUTION
Recall in general
For maximum power, (i) =
(ii) =

## Slide 65: SOLUTION
Rewriting T 4.2 we have T4.3
……T4.3,
But ;
therefore

## Slide 66: TUTORIAL EXAMPLE 5 - POWER FACTOR
= = 0.5
What is to get
Then,

## Slide 67: TUTORIAL EXAMPLE 5 - PHASOR DIAGRAM
Take

## Slide 68: USING SYNCHRONOUS MOTORS FOR POWER FACTOR CORRECTION
The synchronous motor has the ability to draw both lagging and leading current with the through the adjustment of excitation
With under excitation, the motor draws a lagging current
The more frequent mode of operation is with with the motor drawing leading current(the motor behaving like a capacitor – what does a capacitor do?)

## Slide 69: USING SYNCHRONOUS MOTORS FOR POWER FACTOR CORRECTION – cont’d
The motor is thus used as a synchronous condenser for the purpose of power factor correction
In this mode, the motor is run on load and the excitation is adjusted to achieve the level of correction required
Quick trial: Draw the phasor diagrams for leading, lagging and unity pf

## Slide 70: EXAMPLE 4 : CLASS WORK - QUESTION
The most important loads of a production facility are Unit 1 powered by 250kW, 0.6 power factor lagging induction motor and Unit 2, powered by a 150kW, 0.8 power factor lagging motor. These motors are connected in the same lines. It is required to increase the power factor to 0.95 by installing a synchronous motor in parallel with the motors; the synchronous motor drawing 180kW. Calculate the reactive power to be supplied by the motor and its rating in kVA

## Slide 71: SOLUTION
STEP 1: THE POWER FACTOR ANGLES
Unit 1, = 0.6, power factor angle, =
For unit 2, Unit 2, = 0.8, power factor angle, =
The combined power factor, = 0.95, power factor angle, =

## Slide 72: EXAMPLE 4 : CLASS WORK - REACTIVE POWER DRAWN BY RESPECTIVE UNITS (𝑸_𝟏 & 𝑸_𝟐)
Recall S
Where and
or
For Unit 1
)
= 333kVAR
Similarly for Unit 2

## Slide 73: EXAMPLE 4 : CLASS WORK - REACTIVE POWER DRAWN BY RESPECTIVE UNITS (𝑸_𝟏 & 𝑸_𝟐)
Similarly for Unit 2
)
= 113kVAR

## Slide 74: EXAMPLE 4 : CLASS WORK - TOTAL kVAR ( and kW ()
Total Reactive Power,
= 333 + 113
= 446kVAR, this is draw by both inductive motor units
Total system power,

## Slide 75: EXAMPLE 4 : CLASS WORK - TOTAL kVAR ( and kW ()
Total system power,
= 250 + 150 + 180
580kW
Total Reactive power taken from the line

## Slide 76: EXAMPLE 4 : CLASS WORKREACTIVE POWER TO BE DELIVERED BY THE SYNCHRONOUS MOTOR
= 580tan(18.2)
= 191kVAR

## Slide 77: EXAMPLE 4 : CLASS WORK - REACTIVE POWER TO BE DELIVERED BY THE SYNCHRONOUS MOTOR,
= 580tan(18.2)
= 191kVAR

## Slide 78: EXAMPLE 4 : CLASS WORK - SYNCHRONOUS MACHINE RATING IN kVA
= 180kW;
Recall S
=
=
= 312kVA
=
, PF

## Slide 79: EXAMPLE 5 - QUESTION
A 440V, 80kW, Y – connected, 60Hz, four pole synchronous motor with per phase is operating at rated load and 0.8 power factor leading. Its efficiency is 90%. Calculate the:
(i) torque developed
(ii) armature current and power factor
(iii) excitation voltage and power angle
(iv) maximum torque

## Slide 80: EXAMPLE 5 - SOLUTION
Synchronous speed
= 1800rpm
Input power,
88,888.89W
Angular velocity,
188.5 rad.

## Slide 81: EXAMPLE 5 - TORQUE DEVELOPED, T//
= 471.56Nm
Armature Current and

## Slide 82: EXAMPLE 5 - EXCITATION VOLTAGE AND POWER ANGLE
Armature current,
145.8A
623

## Slide 83: EXAMPLE 5 - EXCITATION VOLTAGE AND POWER ANGLE
(iv) for maximum torque,

## Slide 84: Summary for Power Factor Correction Using a Synchronous Motor
A Synchronous Machine when used for the purpose of reactive power control is called a Synchronous Compensator/Condenser/Capacitor.
It is a Synchronous Motor, whose shaft spins freely without any torque on it except its weight.
A Synchronous Machine when used for power factor correction has two circuits;
a Stator Circuit which is connected to the grid and
a Rotor Circuit which is called Field winding/Excitation Winding.

## Slide 85: Summary for Power Factor Correction Using a Synchronous Motor – cont’d
The field winding is controlled by a solid state voltage and frequency regulator.
Increasing the device's field winding excitation results in its furnishing reactive power (VARs) to the system and
decreasing the field winding excitation causes absorption of reactive power from the system (VARs).
Hence, it acts as a capacitor in over excited mode and an as inductor in under-excited mode.
The variations of I with excitation are known as V curves because of their shape.

## Slide 86: SYNCHRONOUS MACHINES V - CURVES
V – curves of a synchronous machines are plots of field current against armature current at various levels of loading.
They apply only to synchronous motors.
There is always a level of excitation, corresponding to unity power factor at which the armature current is minimum
Fig. V shows the V – curves for a synchronous motor
Note: a stability limit exist beyond which stability cannot be maintained during operations; Excitation below this limit causes the motor to pull out of synchronism
V - CURVES
0
50
100
150
100
200
300
400
STABILITY LIMIT
UNITY P.F.
NO LOAD
LAGGING P.F
LEADING P.F
EXCITATION(V)
ARMATURE CURRENT(A)

## Slide 87: TYPICAL SYNCHRONOUS MACHINES V - CURVES

## Slide 88: TYPICAL SYNCHRONOUS MACHINES V - CURVES
A synchronous condenser provides step-less automatic power factor correction with the ability to produce up to 150% additional vars.
The system produces no switching transients and is not affected by system electrical harmonics (some harmonics can even be absorbed by synchronous condensers).
They will not produce excessive voltage levels and are not susceptible to electrical resonances.
Because of the rotating inertia of the synchronous condenser, it can provide real time voltage support during system short circuits.
ADVANTAGES OF A SYNCHRONOUS CONDENSER

## Slide 89: ASSIGNMENTS
1. TESTING SYNCHRONOUS MACHINES
(i) Open circuit test(OCC)
(ii) Short circuit test(SCC)
2. Determination of Synchronous Machine Parameters(synchronous impedance,
3. Zero power factor test(Potier Diagram)
4. Regulation of a synchronous generator

## Slide 90: PARALLEL OPERATION OF GENERATORS
An alternator is an ac generator
In an alternator, an e.m.f is induced in the stator(stationary wire) with the influence of a rotating magnetic field(rotor) due to Faraday’s law of induction.
Due to the synchronous speed of rotation of field poles, it is also known as a synchronous generator
For the parallel operation of an alternator, the efficiency of interconnected ac systems is the focus.

## Slide 91: PARALLEL OPERATION OF GENERATORS
In this case, there shall be more than two alternators connected in parallel in generating stations
There are necessary and sufficient conditions for generators to be connected and operated in parallel
There is also the need to define some terms/terminologies

## Slide 92: DEFINITION OF TERMS
Synchronising/Synchronisation:The process of connecting two alternators or an alternator and an infinite bus bar system in parallel.
2 PARALLEL CONNECTED GENERATORS

## Slide 93: DEFINITION OF TERMS
The Running machine is the machine which carries the load.
2 PARALLEL CONNECTED GENERATORS

## Slide 94: DEFINITION OF TERMS
The Incoming machine is the alternator or machine which has to be connected in parallel with the system.
2 PARALLEL CONNECTED GENERATORS

## Slide 95: Condition for Parallel Operation of Alternator
4 CONDITIONS
The phase sequence of the incoming machine voltage and the bus bar voltage should be identical;
The R.M.S line voltage (terminal voltage) of the bus bar or already running machine and the incoming machine should be the same;
The phase angle of the two systems should be equal; and
The frequency of the two terminal voltages (incoming machine and the bus bar) should be nearly the same.
FURTHER PHASOR/LINE EXPLANATIONS
This three-phase supply consists of three phases, generally represented as R, Y and B or A, B and C
CCW OR +VE
Red OR A
Yellow OR B
Blue OR C

## Slide 96: Condition for Parallel Operation of Alternator
CONDITIONS - 1
The phase sequence of the incoming machine voltage and the bus bar voltage should be identical;
FURTHER PHASOR/LINE EXPLANATIONS
This three-phase supply consists of three phases, generally represented as R, Y and B or A, B and C
CCW OR +VE
Red OR A
Yellow OR B
Blue OR C

## Slide 97: Condition for Parallel Operation of Alternator
CONDITION 2
The R.M.S line voltage (terminal voltage) of the bus bar or already running machine and the incoming machine should be the same;
FURTHER PHASOR/LINE EXPLANATIONS
This three-phase supply consists of three phases, generally represented as R, Y and B or A, B and C
CCW OR +VE
Red OR A
Yellow OR B
Blue OR C

## Slide 98: Condition for Parallel Operation of Alternator
CONDITION 3
The phase angle of the two systems should be equal; and
FURTHER PHASOR/LINE EXPLANATIONS
This three-phase supply consists of three phases, generally represented as R, Y and B or A, B and C
Red OR A
CCW OR +VE
Yellow OR B
Blue OR C

## Slide 99: Condition for Parallel Operation of Alternator
CONDITION - 4
The frequency of the two terminal voltages (incoming machine and the bus bar) should be nearly the same.
FURTHER PHASOR/LINE EXPLANATIONS
This three-phase supply consists of three phases, generally represented as R, Y and B or A, B and C
CCW OR +VE
Red OR A
Yellow OR B
Blue OR C

## Slide 100: WHY WE MUST STRICTLY ADHERE TO ALL THE 4 CONDITIONS
Large power transients will occur when frequencies are not nearly equal.
Departure from the above conditions will result in the formation of power surges and current.
It also results in unwanted electro-mechanical oscillation of rotor which leads to the damage of equipment.

## Slide 101: General Procedure for Paralleling Alternators
Intro to procedure
The figure shows an alternator (generator 2) being paralleled with a running power system (generator 1).
These two machines are about to synchronize for supplying power to a load.
Generator 2 is about to parallel with the help of a switch, S1.
This switch should never be closed without satisfying the above conditions
Connection diagram

## Slide 102: General Procedure for Paralleling Alternators – cont’d
Procedure
To make the terminal voltages equal. This can be done by adjusting the terminal voltage of incoming machine by changing the field current and make it equal to the line voltage of running system using voltmeters.
There are two methods to check the phase sequence of the machines.
2 methods to check phase sequence
They are as follows
  First one is using a Synchroscope. It is not actually check the phase sequence but it is used to measure the difference in phase angles.
Second method is three lamp method (Figure 2). Here we can see three light bulbs are connected to the terminals of the switch, S1. Bulbs become bright if the phase difference is large. Bulbs become dim if the phase difference is small. The bulbs will show dim and bright all together if phase sequence is the same. The bulbs will get bright in progression if the phase sequence is opposite. This phase sequence can be made equal by swapping the connections on any two phases on one of the generators

## Slide 103: General Procedure for Paralleling Alternators – cont’d
Next, we have to check and verify the incoming and running system frequency. It should be nearly the same. This can be done by inspecting the frequency of dimming and brightening of lamps.
When the frequencies are nearly equal, the two voltages (incoming alternator and running system) will alter the phase gradually. These changes can be observed and the switch, S1 can be made closed when the phase angles are equal.

## Slide 104: Advantages of Parallel Operating Alternators
When there is maintenance or an inspection, one machine can be taken out from service and the other alternators can keep up for the continuity of supply.
Load supply can be increased.
During light loads, more than one alternator can be shut down while the other will operate in nearly full load.
High efficiency.
The operating cost is reduced.
Ensures the protection of supply and enables cost-effective generation.
The generation cost is reduced.
Breaking down of a generator does not cause any interruption in the supply.
Reliability of the whole power system increases.

## Slide 105: MOTORS AND THEIR USES – COST VS APPLICATION VS TECHNOLOGY(AC/DC)

## Slide 106: AC MOTORS
AC motors are highly flexible in many features including speed control (VSD Variable Speed Drives)
they have a much larger installed base compared to DC motors,
The current trend for VSD is to add more features and programmable logic control (PLC) functionality,
these are advantages for the experienced used, but require greater technical expertise during maintenance.
some of the key advantages are:
Low power demand on start
Controlled acceleration
Adjustable operational speed
Controlled starting current
Adjustable torque limit
Reduced power line disturbances

## Slide 107: TYPES OF AC MOTORS AND APPLICATIONS
Synchronous
the rotation of the rotor is synchronized with the frequency of the supply current ;
the speed remains constant under varying loads;
It is ideal for driving equipment at a constant speed; and
They are used in high precision positioning devices like robots, instrumentation, machines and process control
Induction (Asynchronous)
uses electromagnetic induction from the magnetic field of the stator winding to produce an electric current in the rotor and hence Torque;
These are the most common type of AC motor and important in industry due to their load capacity with Single-Phase induction motors being used mainly for smaller loads, like used in house hold appliances whereas
Three-Phase induction motors are used more in industrial applications including like compressors, pumps, conveyor systems and lifting gear.

## Slide 108: GENERATOR TYPES AND APPLICATIONS
POWER STATION & TRAILER MOUNTED
In grid system for public supply networks, a number of high power generator sets may operate in parallel from different power station;
Some portable supplies, often trailer-mounted, where alternative supply system is not available.
PRIVATE/INDEPENDENT/standby
Sometimes private or independent generators may run in parallel with the public supply system or isolated from it when demand is less e.g peak shaving to reduce the maximum demand for electricity consumed by a user and this can avoid large financial penalties during times of normally high demand on the grid system;
Keep standby or emergency generators to protect the supply to the critical circuits such as hospitals, fire service, and water supply system;
Some time is required some temporary supply system by the construction industry or in cases of any breakdown.

## Slide 109: GENERATOR TYPES AND APPLICATIONS
Solar generator
-Solar powered generators are great replacement for traditional gas powered models. These are perfect for indoor use. They are also capable supplying direct current. So theses are perfect for camping, RV's and specifically designed low voltage appliances for a residence. These generators designed to supply electrical power for compatible electrical.
Residential stand by generator
-These generators are very efficient. Portable generators can provide critical backup power in an emergency situation. These generator generic pressure washers give you the power to clean everything around the house.

## Slide 110: GENERATOR TYPES AND APPLICATIONS
Commercial stand by generator
It is a worldwide power generator system. It has switchgear, automatic transfer switches and paralleling equipment. These are used in a very large scale. These are quite same as residential generators and starts at 30,000 watts
Industrial generator-They
They achieve efficiency levels of up to 99 percent. These industrial generators are available in different types like natural gas, diesel, and many more. For the industrial companies, the installation of industrial generator is very essential.